WESLEY COURT FIRE RISK ASSESSMENT Dated 26th September 2024

OVERVIEW OF PROGRESS AT 30th June 2025

| Number | Issue | Priority | Current Status |
| --- | --- | --- | --- |
| 1 | Regular EIRCs to be conducted | 1,A High | Completed - 24-7-23 report (5 yearly) |
| 2 | PAT Testing (vacuum cleaner) | 3, Low | Completed – hoover removed |
| 3 | Bin store contents – mattress, fuel can | 3, Medium | Completed - items removed |
| 4 | External cladding of building (NB building lower than 12m high so not legal requirement) | 3, Low | Independent cladding spec received. Plan for next phase of replacement agreed, work scheduled to start 14th July 2025 to bring replacement of cladding to 50% of building. |
| 5 | Fire extinguishers in store room | 3, low | Completed – items removed |
| 6 | Flat front doors not compliant (No 16 & No 22 | 1, Medium | Doors fitted by contractor replaced 8th March 2025(No 22), No 16 planned. |
| 7 | Flat No 27 – hasp across front door | 3, Urgent | Completed – door replaced hasp removed |
| 8 | Foam around cables into storerooms not clearly fire regs compliant | 3, Medium | Foam confirmed to be compliant by fitter. |
| 9 | Training of flat occupants on fire alarms | 0-3, Urgent | Annual communication finalised and distributed March 2025 |
| 10 | Fire alarm zonal map needed next to fire alarm panel | 3, Low risk | Completed – already present and now also on central noticeboard |
| 11 | See No 9 above, occupants must be advised of fire alarm and fire safety procedures | 0-3, High, Annually | Annual communication finalised and distributed March 2025. |
| 12 | Residents (and owners) to be advised that front doors must be compliant and not altered | 0-2, High, Annually | Completed for owners. Annual communication finalised and distributed March 2025 |
| 13 | Block to be managed in accordance with fire regulations | 0, High, Ongoing | Completed – see FRA and ongoing |
| 14 | Fire alarm action notices must reflect Stay Put policy | 3, Medium | Completed – see notices. Also added to annual advice notices |
| 15 | Contractors Policy, including Hot Works Policy | 0-2, Med/low | Policies signed off March 2025 |
| 16 | Fire extinguisher servicing out of date | 3, Low | Completed – fire extinguishers removed |
| 17 | Fire Alarm testing required every 6 months | 0, Weekly, 6 Monthly | Now Weekly and six monthly testing. Reviewed by Directors May 2025. |
| 18 | Emergency Lighting testing required monthly and annually | 0, Monthly Annually | Completed – current procedures comply |
| 19 | Flat front doors and communal fire doors must be compliant with Fire Regs and regularly inspected | 0-2, Urgent | Mgt Committee asked owners to audit and certify their front doors June 2025 |
| 20 | Flat No 22 replacement front door not compliant with fire regs | 0-2, Urgent | Front door replaced 8 March 2025, certified compliant June 2025 |
| 21 | All tests and inspections to be completed and recorded and records to be available | Ongoing | Completed – all log books are kept on site for inspection |